## Slide 1
AIR

## Slide 20
Classifications of Pumps
We can classify pumps in different ways;
by their range of pressures,
their means of operation,
their cleanliness,
their ability to pump a continuous gas flow, and
their ability to pump different gases.
We will next discuss each of these classifications and summarize the several types of pumps in Table 6.1.

## Slide 21
Pumps can be broadly categorized according to three techniques
Positive displacement pumps use a mechanism to repeatedly expand a cavity, allow gases to flow in from the chamber, seal off the cavity, and exhaust it to the atmosphere.
Momentum transfer pumps, also called molecular pumps, use high speed jets of dense fluid or high speed rotating blades to knock gas molecules out of the chamber.
Entrapment pumps capture gases in a solid or adsorbed state. This includes cryopumps, getters, and ion pumps.
Types

## Slide 22
Vacuum pump
A vacuum pump is a device that removes gas molecules from a sealed volume in order to leave behind a partial vacuum.
The first vacuum pump was invented in 1650 by Otto von Guericke, and was preceded by the suction pump, which dates to antiquity.

## Slide 23
Positive displacement pumps are the most effective for low vacuums.
Momentum transfer pumps in conjunction with one or two positive displacement pumps are the most common configuration used to achieve high vacuums.
In this configuration the positive displacement pump serves two purposes.
First it obtains a rough vacuum in the vessel being evacuated before the momentum transfer pump can be used to obtain the high vacuum, as momentum transfer pumps cannot start pumping at atmospheric pressures.
Second the positive displacement pump backs up the momentum transfer pump by evacuating to low vacuum the accumulation of displaced molecules in the high vacuum pump.
Entrapment pumps can be added to reach ultrahigh vacuums, but they require periodic regeneration of the surfaces that trap air molecules or ions. and vibration.

## Slide 24
Due to this requirement their available operational time can be unacceptably short in low and high vacuums, thus limiting their use to ultrahigh vacuums.
Pumps also differ in details like manufacturing tolerances, sealing material, pressure, flow, admission or no admission of oil vapor, service intervals, reliability, tolerance to dust, tolerance to chemicals, tolerance to liquids

## Slide 25
Performance measures
Pumping speed refers to the volume flow rate of a pump at its inlet, often measured in volume per unit of time.
Momentum transfer and entrapment pumps are more effective on some gases than others, so the pumping rate can be different for each of the gases being pumped, and the average volume flow rate of the pump will vary depending on the chemical composition of the gases remaining in the chamber.
Throughput refers to the pumping speed multiplied by the gas pressure at the inlet, and is measured in units of pressure·volume/unit time.
At a constant temperature, throughput is proportional to the number of molecules being pumped per unit time, and therefore to the mass flow rate of the pump.

## Slide 26
When discussing a leak in the system or back streaming through the pump, throughput refers to the volume leak rate multiplied by the pressure at the vacuum side of the leak, so the leak throughput can be compared to the pump throughput.
Positive displacement and momentum transfer pumps have a constant volume flow rate (pumping speed), but as the chamber's pressure drops, this volume contains less and less mass.
So although the pumping speed remains constant, the throughput and mass flow rate drop exponentially.
Meanwhile, the leakage, evaporation, sublimation and back streaming rates continue to produce a constant throughput into the system.

## Slide 47
Introduction to Vacuum Pumps
Exactly how do we produce a vacuum?
Many different kinds of vacuum pumps exist, each with their own application.
The most common types of pumps are the rotary pump for reaching rough vacuum, and the diffusion pump for reaching high vacuum.
These will be discussed rest followed by other pumps.
For each pump we need to discuss several things:
1. How it operates.
2. What pressure range it operates in.
3. Its pumping speed.
4. Type of gas ow (viscous or molecular).
5. Eects of pumping on dierent types of gas.
6. Advantages and disadvantages.

## Slide 48
Three methods of drawing vacuum components are common.
The rest uses sketches that are approximately realistic.
You can see an example of this in the typical vacuum system shown on the left hand side of Figure 5.5 in the previous chapter.
The second method uses standard symbols of the American Vacuum Society.
The third method uses standard symbols found in Europe.
We will show these symbols as we go through the discussion of the pumps.

## Slide 56
Compressed Air Distribution
A poorly designed and carelessly installed pneumatic distribution system will cause trouble and result in expensive repairs and costly down-time.
A well designed system, however, provides relatively clean air at the necessary pressure to efficiently operate the components at maximum production capabilities.
Here are some things to consider when planning a pneumatic distribution system.**
1. Both a general purpose pre-filter and an oil filter and an oil removal filter should be installed just downstream of the compressor after cooler to remove solid contaminants, water and oil. (Water, of course, promotes corrosion and, in combination with other contaminants, forms sludge). A dryer should be installed between the after cooler and receiver.

## Slide 57
2. Pressure drop between the receiver and the point of use should be kept at a minimum. The loss should be 3% or less of the line pressure.
3. Pipe sizing is an important factor.You must remember the relationship between pressure drop and air flow. For a given size of line, pressure losses increase as flow increases. Main lines should be sized with future requirements and the effects of aging in mind.
As systems age, rust and corrosion affect the inside smoothness of pipe walls causing additional pressure loss. Specify pipe sizes so that pressure drop between the receiver and the farthest point of use in the system is less than 3% of the original line pressure.
Branch mains and drop lines should be large enough to handle “peak” compressed air needs

## Slide 58
4. An additional accumulator of liberal size should be installed where distribution lines are long. This unit should be mounted at the farthest point from the main receiver. In many installations the demand for air comes in short, heavy bursts. This additional air supply at the end of the line will help to maintain system pressure.
5. Main filters, those with screens or coarse filter elements, should be mounted in the mail distribution line after the receiver. Element rating is 50 to 70 microns. Smaller branch or drop line filters should be used throughout the distribution system and be installed as close as possible to the equipment to be protected. These filters are rated 5 to 50 microns. As a general rule, the distance between a drop line filter and the equipment it is to protect should not exceed 20 feet.

## Slide 59
6. When installing new piping systems, main lines should slope 1⁄8 to 1⁄4" per foot down from the point of origin. Gravity and airflow will then carry condensate to the low points where drop leg should be installed to allow for removal. These drops should be installed every 50 to 70 feet in the system and be taken from the bottom of the main line to insure as much removal as possible.
On extremely long lines, the configuration shown can be used to compensate for sloping lines.
Drip leg drains should be installed at low points in the piping and at the far end of the distribution system where water is likely to accumulate.
A 1⁄2" globe valve should be installed in the drop line just before the drain so that the unit can be isolated for maintenance without shutting off the air pressure in the remainder of the piping system.
The drip leg drain should be cleaned periodically. Most units can be disassembled for maintenance without removal from the air line.
SHUT OFF AIR AND REDUCE PRESSURE TO ZERO BEFORE DISASSEMBLING.

## Slide 60
7. The air line drops are taken from the top of the main line. This prevents any condensate which forms in the main line from following into the branch lines.
8. Individual shut-off valves should be installed at each drop line to isolate it from the rest of the system for maintenance.
9. The air should be filtered at each work station to remove any additional water (which may have condensed in the main and ranch lines due to cooling of the air), rust, sludge, pipe scale and other contaminants (some of which are introduced at the time the system is constructed).
Tight, secure pipe joints prevent leaks that waste compressed air. If a main air line dryer is used, there should not be any additional condensed moisture unless the air temperature goes below the dew point setting of the dryer.

## Slide 63
Compressed Air Filtration

## Slide 64
Compressed Air Regulation